1. Current building floor plan

2. Emergency fire evacuation plan

Reviewed within last 2 years.

(1)	Use of alarms

(2)	Transmission of alarms to fire department

(3)	Emergency phone call to fire department

(4)	Response to alarms

(5)	Isolation of fire

(6)	Evacuation of immediate area

(7)	Evacuation of smoke compartment

(8)	Preparation of floors and building for evacuation

(9) Extinguishment of fire

3. Smoking regulations/policy

Reviewed within last 2 years.

4. Fire drill records

Quarterly on each shift

Drills held at varying times/ If NH & Hosp

For example, are connected drills must.

Be held separately.

5. Out-of-service policies

Fire Alarm out of Service 4 hours

Fire Sprinkler put of Service 10 hours.

Correct contact information

6. Fire alarm system

Monthly D.A.C.T Tests Annual Inspection Report/NFPA 72 Form/Equal

Semi-Annual Visual Inspection

7. Smoke detector sensitivity testing

Must show the sensitivity range, and the actual tested sensitivity for each                      smoke detector, and test date(s).

8. Resident room smoke detectors

Tested weekly/monthly per manufacturer recommendations (If battery operated)

9. Fire sprinkler system

Quarterly test (in house/vendor)

Annual vendor test date

NFPA 25 form(s)

5-year Obstruction/Internal

Piping/gauge replacement

Water supply source

Fire Pump testing- weekly/annual

10. Range hood system inspection

Semi-annual inspection dates

System activates fire alarm system.

11. Fire Extinguisher

Monthly in-house inspection date

Annual vendor service date

6 yr. maintenance date

12 yr. hydrostatic test date

Inventory log

12. Generator

Weekly visual

Monthly 30-minute load test

Documented 5-minute Cool down.

Annual Load Bank if Diesel

Letter of Reliability if Natural Gas

36 Month 4 Hour Load Bank Test-All Fuel

Fuel Sampling-Diesel

13. Battery emergency light testing

Monthly 30 second test

Annual 90-minute test

14. Smoke Damper Testing

Every 4 Years Nursing Home

Every 6 Years Hospital

15. Flame spread documentation

Wall, ceiling & floor finishes Drapes, cubicle curtains decorations

16. Upholstered furniture flammability·

California Tech. Bulletin 133 or 117 NFPA 266, Upholstered Furniture Note: Documentation for numbers 15 &    16 must be kept on file for the life of the items   or material. All other documentation shall be kept at least two years, or longer when 4-, 6-, & 12-year intervals apply.

17. Door Inspections

13-point inspection documented on all                 Fire Doors-Annually

18. Med Gas Training

All personnel in contact with med gas will have continuing education on handling and    storage of med gas.

19. Risk Assessment Documentation

Per NFPA 99 Any changes to facility will       require an update

NFPA 99 Chapter 5, 6, 9, 10 &11

20. Space Heater Policy

If you allow them, you MUST have a policy.

That states NOT in patient care areas.

21. Lab Procedures/Incidents

22. Electrical Receptacle Testing

Completed Annually